{"text_format":"3","workbook":"xlsx","n_sheets":4,"sheets":["（清单）单位工程费汇总表","（清单）分部分项工程量清单与计价表","（清单）措施项目清单报价表（一）","（清单）措施项目清单报价表（二）"],"read":"whole","date_system":"1900"}

{"sheet":"（清单）单位工程费汇总表","index":0,"n_rows":22,"n_cols":7,"rows_kept":22,"merged":[[0,0,0,6],[1,0,1,2],[1,4,1,6],[2,2,2,4],[3,2,3,4],[4,2,4,4],[5,2,5,4],[6,2,6,4],[7,2,7,4],[8,2,8,4],[9,2,9,4],[10,2,10,4],[11,2,11,4],[12,2,12,4],[13,2,13,4],[14,2,14,4],[15,2,15,4],[16,2,16,4],[17,2,17,4],[18,2,18,4],[19,2,19,4],[20,2,20,4],[21,2,21,4],[22,2,22,4],[23,2,23,4],[24,2,24,4],[25,2,25,4],[26,2,26,4],[27,2,27,4],[28,2,28,4],[29,2,29,4],[30,2,30,4],[31,2,31,4],[32,2,32,4],[33,2,33,4],[34,2,34,4],[35,2,35,4],[36,2,36,4],[37,2,37,4]]}
["工程量清单报价汇总表"]
["工程名称：厚街镇厚山现代化产业园产业空间开发项目新建3台630kVA临时箱变安装工程",{"$nulls":3},"第 1 页  共 1 页"]
["序号","费用名称","基数说明",null,null,"费率(%)","金额"]
["1","分部分项合计","分部分项合计"]
["2","措施合计","绿色施工安全防护措施费+其他措施费"]
["2.1","绿色施工安全防护措施费","安全及文明施工措施费"]
["2.2","其他措施费","其他措施费"]
["3","其他项目","其他项目合计"]
["3.1","暂列金额","暂列金额"]
["3.2","暂估价","暂估价合计"]
["3.3","计日工","计日工"]
["3.4","总承包服务费","总承包服务费"]
["3.5","预算包干费","分部分项人工费+分部分项机具费"]
["3.6","工程优质费","工程优质费"]
["3.7","概算幅度差","概算幅度差"]
["3.8","索赔费用","索赔费用"]
["3.9","现场签证费用","现场签证费用"]
["3.10","其他费用","其他费用"]
["4","税前工程造价","分部分项合计+措施合计+其他项目"]
["5","增值税销项税额","分部分项合计+措施合计+其他项目"]
["6","总造价","分部分项合计+措施合计+其他项目+增值税销项税额"]
["7","人工费","分部分项人工费+技术措施项目人工费+机上人工费"]

{"sheet":"（清单）分部分项工程量清单与计价表","index":1,"n_rows":80,"n_cols":10,"rows_kept":80,"merged":[[0,0,0,9],[1,0,1,4],[1,5,1,6],[1,7,1,9],[2,0,3,0],[2,1,3,1],[2,2,3,2],[2,3,3,3],[2,4,3,5],[2,6,3,7],[2,8,2,9],[4,2,4,3],[4,4,4,5],[4,6,4,7],[5,4,5,5],[5,6,5,7],[6,4,6,5],[6,6,6,7],[7,4,7,5],[7,6,7,7],[8,4,8,5],[8,6,8,7],[9,4,9,5],[9,6,9,7],[10,4,10,5],[10,6,10,7],[11,4,11,5],[11,6,11,7],[12,4,12,5],[12,6,12,7],[13,4,13,5],[13,6,13,7],[14,4,14,5],[14,6,14,7],[15,0,15,8],[16,0,16,4],[16,5,16,6],[16,7,16,9],[17,0,17,4],[17,5,17,6],[17,7,17,9],[18,0,18,9],[19,0,19,4],[19,5,19,6],[19,7,19,9],[20,0,21,0],[20,1,21,1],[20,2,21,2],[20,3,21,3],[20,4,21,5],[20,6,21,7],[20,8,20,9],[22,4,22,5],[22,6,22,7],[23,4,23,5],[23,6,23,7],[24,4,24,5],[24,6,24,7],[25,4,25,5],[25,6,25,7],[26,4,26,5],[26,6,26,7],[27,4,27,5],[27,6,27,7],[28,4,28,5],[28,6,28,7],[29,4,29,5],[29,6,29,7],[30,0,30,8],[31,0,31,4],[31,5,31,6],[31,7,31,9],[32,0,32,4],[32,5,32,6],[32,7,32,9],[33,0,33,9],[34,0,34,4],[34,5,34,6],[34,7,34,9],[35,0,36,0],[35,1,36,1],[35,2,36,2],[35,3,36,3],[35,4,36,5],[35,6,36,7],[35,8,35,9],[37,4,37,5],[37,6,37,7],[38,4,38,5],[38,6,38,7],[39,4,39,5],[39,6,39,7],[40,4,40,5],[40,6,40,7],[41,2,41,3],[41,4,41,5],[41,6,41,7],[42,2,42,3],[42,4,42,5],[42,6,42,7],[43,4,43,5],[43,6,43,7],[44,4,44,5],[44,6,44,7],[45,4,45,5],[45,6,45,7],[46,4,46,5],[46,6,46,7],[47,4,47,5],[47,6,47,7],[48,4,48,5],[48,6,48,7],[49,0,49,8],[50,0,50,4],[50,5,50,6],[50,7,50,9],[51,0,51,4],[51,5,51,6],[51,7,51,9],[52,0,52,9],[53,0,53,4],[53,5,53,6],[53,7,53,9],[54,0,55,0],[54,1,55,1],[54,2,55,2],[54,3,55,3],[54,4,55,5],[54,6,55,7],[54,8,54,9],[56,4,56,5],[56,6,56,7],[57,4,57,5],[57,6,57,7],[58,2,58,3],[58,4,58,5],[58,6,58,7],[59,2,59,3],[59,4,59,5],[59,6,59,7],[60,4,60,5],[60,6,60,7],[61,4,61,5],[61,6,61,7],[62,4,62,5],[62,6,62,7],[63,2,63,3],[63,4,63,5],[63,6,63,7],[64,4,64,5],[64,6,64,7],[65,4,65,5],[65,6,65,7],[66,4,66,5],[66,6,66,7],[67,4,67,5],[67,6,67,7],[68,4,68,5],[68,6,68,7],[69,4,69,5],[69,6,69,7],[70,4,70,5],[70,6,70,7],[71,4,71,5],[71,6,71,7],[72,4,72,5],[72,6,72,7],[73,4,73,5],[73,6,73,7],[74,4,74,5],[74,6,74,7],[75,4,75,5],[75,6,75,7],[76,0,76,8],[77,0,77,8],[78,0,78,4],[78,5,78,6],[78,7,78,9],[79,0,79,4],[79,5,79,6],[79,7,79,9]]}
["分部分项工程量清单报价表"]
["工程名称：厚街镇厚山现代化产业园产业空间开发项目新建3台630kVA临时箱变安装工程",{"$nulls":6},"(编制单位盖章)"]
["序号","项目编码","项目名称","项目特征描述","计量\n单位",null,"工程量",null,"金额（元）"]
[{"$nulls":8},"综合单价","合价"]
[null,null,"   10kV进线环网电缆工程"]
[1,"030408001001","电力电缆","1.名称:电力电缆\n2.规格、型号:ZCYJV22-3*120mm2\n3.材质:铜芯\n4.敷设方式、部位:按实考虑\n5.电压等级(kV):8.7/15kV\n6.符合设计图纸、施工规范要求","m",null,"365"]
[2,"030408001002","电力电缆","1.名称:电力电缆\n2.规格:ZCYJV22-3*95mm2\n3.材质:铜芯\n4.敷设方式、部位:按实考虑\n5.电压等级(kV):8.7/15kV\n6.符合设计图纸、施工规范要求","m",null,"32"]
[3,"030408006001","10kV户内冷缩式铜芯电缆终端头 3*120mm2","1.名称:电缆终端头\n2.规格:3*120mm2\n3.材质、类型:铜芯、冷缩式\n4.安装部位:户内\n5.电压等级(kV):10kV\n6.符合设计图纸、施工规范要求","个",null,"2"]
[4,"030408006002","10kV户内冷缩式铜芯电缆终端头 3*95mm2","1.名称:电缆终端头\n2.规格:3*95mm2\n3.材质、类型:铜芯、冷缩式\n4.安装部位:户内\n5.电压等级(kV):10kV\n6.符合设计图纸、施工规范要求","个",null,"4"]
[5,"030408006003","10kV户外冷缩式铜芯电缆终端头 3*120mm2","1.名称:电缆终端头\n2.规格:3*120mm2\n3.材质、类型:铜芯、冷缩式\n4.安装部位:户外\n5.电压等级(kV):10kV\n6.符合设计图纸、施工规范要求","个",null,"1"]
[6,"030408006004","10kV热熔铜芯电缆中间头 3*120mm2","1.名称:电缆中间头\n2.规格:3*120mm2\n3.材质、类型:铜芯、热熔式\n4.安装部位:户外\n5.电压等级(kV):10kV\n6.含中间头防爆盒\n7.符合设计图纸、施工规范要求","个",null,"1"]
[7,"030402002001","真空断路器","1.名称:看门狗\n2.符合设计图纸、施工规范要求","台",null,"1"]
[8,"030408008003","电缆穿墙孔洞防火封堵（800*600）","1.名称:电缆穿墙孔洞防火封堵（800*600）\n2.符合设计图纸、施工规范要求","处",null,"16"]
[9,"030408008002","开关柜进线孔防火封堵（700*800）","1.名称:开关柜进线孔防火封堵（700*800）\n2.符合设计图纸、施工规范要求","处",null,"3"]
[10,"040501008001","1线顶管 HDPE管φ160*8","1.名称:1线顶管\n2.材质:HDPE管\n3.规格:φ160,壁厚8mm厚\n4.接口方式:熔接\n5.泥浆要求:按规范要求\n6.符合设计图纸、施工规范要求","m",null,"342"]
["本页小计"]
["编制人：                           证号：",{"$nulls":6},"编制日期：   年   月   日"]
[{"$nulls":7},"第 1 页  共 4 页"]
["分部分项工程量清单报价表"]
["工程名称：厚街镇厚山现代化产业园产业空间开发项目新建3台630kVA临时箱变安装工程",{"$nulls":6},"(编制单位盖章)"]
["序号","项目编码","项目名称","项目特征描述","计量\n单位",null,"工程量",null,"金额（元）"]
[{"$nulls":8},"综合单价","合价"]
[11,"040504001001","1层1列排管直线井","1.名称:1层1列排管直线井\n2.集水口:PVC200塑料管,内填细砂\n3.垫层:100mm厚C15砼垫层\n4.底板:C25砼底板\n5.井壁:C25砼井壁\n6.抹灰:15mm厚1:2.5水泥防水砂浆抹面\n7.压顶:C30砼压顶\n8.盖板:C30预制盖板 1150*300*150mm,5mm厚C型钢包边\n9.其它:预埋镀锌角钢L50*5,标志牌\n10.橡胶缓冲层\n11.钢筋:按设计图纸\n12.符合设计图纸、施工规范要求","座",null,"7"]
[12,"040504001002","1层1列排管直线长井","1.名称:1层1列排管直线长井\n2.集水口:PVC200塑料管,内填细砂\n3.垫层:100mm厚C15砼垫层\n4.底板:C25砼底板\n5.井壁:C25砼井壁\n6.抹灰:15mm厚1:2.5水泥防水砂浆抹面\n7.压顶:C30砼压顶\n8.盖板:C30预制盖板 1150*300*150mm,5mm厚C型钢包边\n9.其它:预埋镀锌角钢L50*5,标志牌\n10.橡胶缓冲层\n11.钢筋:按设计图纸\n12.符合设计图纸、施工规范要求","座",null,"1"]
[13,"041001001002","拆除路面","1.材质:拆除混凝土路面\n2.厚度:20cm\n3.含路面切缝\n4.废料运距:由投标单位自行考虑\n5.符合设计图纸、施工规范要求","m2",null,"69.09"]
[14,"040203007002","水泥混凝土","1.混凝土强度等级:C30混凝土\n2.厚度:20cm\n3.水养生\n4.符合设计图纸、施工规范要求","m2",null,"69.09"]
[15,"040101002001","挖沟槽土方","1.土壤类别:综合考虑\n2.挖土深度:2m 内\n3.符合设计图纸、施工规范要求","m3",null,"46.82"]
[16,"040103001001","回填方","1.密实度要求:按规范要求\n2.填方材料品种:原土回填\n3.符合设计图纸、施工规范要求","m3",null,"8.06"]
[17,"040103001002","回填方","1.密实度要求:按规范要求\n2.填方材料品种:回填石粉\n3.符合设计图纸、施工规范要求","m3",null,"8.77"]
[18,"040103002001","余方弃置","1.废弃料品种:一般土壤和碎(砾)石\n2.运距:由投标单位自行考虑\n3.符合设计图纸、施工规范要求","m3",null,"38.76"]
["本页小计"]
["编制人：                           证号：",{"$nulls":6},"编制日期：   年   月   日"]
[{"$nulls":7},"第 2 页  共 4 页"]
["分部分项工程量清单报价表"]
["工程名称：厚街镇厚山现代化产业园产业空间开发项目新建3台630kVA临时箱变安装工程",{"$nulls":6},"(编制单位盖章)"]
["序号","项目编码","项目名称","项目特征描述","计量\n单位",null,"工程量",null,"金额（元）"]
[{"$nulls":8},"综合单价","合价"]
[19,"040205004001","标志桩","1.类型:电缆标桩\n2.规格尺寸:400*100*100\n3.材质:C20砼\n4.符合设计图纸、施工规范要求","块",null,"30"]
[20,"030414015001","电缆试验","1.名称:10kV电缆交流耐压试验\n2.符合设计图纸、施工规范要求","次",null,"3"]
[21,"030414015002","电缆试验","1.名称:电缆局放试验\n2.电压等级(kV):10kV\n3.符合设计图纸、施工规范要求","次",null,"3"]
[22,"030414015003","临时设备、临时电缆拆除及回收","1.名称:临时设备、临时电缆拆除及回收\n2.符合设计图纸、施工规范要求","项",null,"1"]
[null,null,"【10kV进线环网电缆工程】分部小计"]
[null,null,"   高低压配电工程"]
[23,"030408001004","电力电缆","1.名称:电力电缆\n2.规格、型号:ZCYJV22-3*70mm2\n3.材质:铜芯\n4.敷设方式、部位:按实考虑\n5.电压等级(kV):8.7/15kV\n6.工程量暂定\n7.符合设计图纸、施工规范要求","m",null,"24"]
[24,"030408006006","10kV户内冷缩式铜芯电缆终端头 3*70mm2","1.名称:电缆终端头\n2.规格:3*70mm2\n3.材质、类型:铜芯、冷缩式\n4.安装部位:户内\n5.电压等级(kV):10kV\n6.符合设计图纸、施工规范要求","个",null,"6"]
[25,"030402018001","1#组合型成套箱式变电站 S11-M-630kVA","1.名称:1#组合型成套箱式变电站\n2.型号:S11-M-630kVA\n3.符合设计图纸、施工规范要求","台",null,"1"]
[26,"030402018002","2#组合型成套箱式变电站 S11-M-630kVA","1.名称:2#组合型成套箱式变电站\n2.型号:S11-M-630kVA\n3.符合设计图纸、施工规范要求","台",null,"1"]
[27,"030402018003","3#组合型成套箱式变电站 S11-M-630kVA","1.名称:3#组合型成套箱式变电站\n2.型号:S11-M-630kVA\n3.符合设计图纸、施工规范要求","台",null,"1"]
[28,"040801003001","箱变基础","1.名称:箱变基础\n2.型号:S11-M-630kVA\n3.垫层:200mm厚C15\n4.基础:C25\n5.抹灰:20mm厚1:2水泥防水砂浆抹面\n6.基础形式、材质、规格:含通风钢网\n7.含人孔井,台阶\n8.含土石方工程\n9.符合设计图纸、施工规范要求","台",null,"3"]
["本页小计"]
["编制人：                           证号：",{"$nulls":6},"编制日期：   年   月   日"]
[{"$nulls":7},"第 3 页  共 4 页"]
["分部分项工程量清单报价表"]
["工程名称：厚街镇厚山现代化产业园产业空间开发项目新建3台630kVA临时箱变安装工程",{"$nulls":6},"(编制单位盖章)"]
["序号","项目编码","项目名称","项目特征描述","计量\n单位",null,"工程量",null,"金额（元）"]
[{"$nulls":8},"综合单价","合价"]
[29,"040801003002","箱变护栏","1.名称:箱变护栏\n2.垫层:60mm厚C15\n3.基础:C25\n4.底座:C25\n5.含镀锌钢管、镀锌方通、钢网围栏、安全标识牌、镀锌钢合页\n6.70mm厚本色透水混凝土面层,30mm厚细碎石过滤层,150mm厚碎石基层\n7.符合设计图纸、施工规范要求","台",null,"3"]
[30,"030414001001","组合型成套箱式变电站系统","1.名称:组合型成套箱式变电站系统调试\n2.容量(kV.A):1000kVA以下\n3.符合设计图纸、施工规范要求","系统",null,"3"]
[null,null,"【高低压配电工程】分部小计"]
[null,null,"   其他配套工程"]
[31,"040801003003","箱变接地","1.名称:箱变接地\n2.角钢垂地极:镀锌角钢L50X5X2500\n3.圆钢水平地极:热镀锌φ16\n4.圆钢引出线:热镀锌φ16\n5.符合设计图纸、施工规范要求","台",null,"3"]
[32,"030414011001","接地装置调试","1.名称:接地装置调试\n2.类别:独立接地装置\n3.符合设计图纸、施工规范要求","系统",null,"3"]
[33,"030414014001","安健环标识","1.名称:安健环标识牌\n2.备注:各类门牌、警示牌、标识等\n3.符合设计图纸、施工规范要求","套",null,"3"]
[null,null,"【其他配套工程】分部小计"]
{"$rows_empty":12}
["本页小计"]
["合  计"]
["编制人：                           证号：",{"$nulls":6},"编制日期：   年   月   日"]
[{"$nulls":7},"第 4 页  共 4 页"]

{"sheet":"（清单）措施项目清单报价表（一）","index":2,"n_rows":35,"n_cols":7,"rows_kept":35,"merged":[[0,0,0,6],[1,0,1,4],[1,5,1,6],[2,2,2,3],[2,4,2,5],[3,2,3,3],[3,4,3,5],[4,2,4,3],[4,4,4,5],[5,2,5,3],[5,4,5,5],[6,2,6,3],[6,4,6,5],[7,2,7,3],[7,4,7,5],[8,2,8,3],[8,4,8,5],[9,2,9,3],[9,4,9,5],[10,2,10,3],[10,4,10,5],[11,2,11,3],[11,4,11,5],[12,2,12,3],[12,4,12,5],[13,2,13,3],[13,4,13,5],[14,2,14,3],[14,4,14,5],[15,2,15,3],[15,4,15,5],[16,2,16,3],[16,4,16,5],[17,2,17,3],[17,4,17,5],[18,2,18,3],[18,4,18,5],[19,2,19,3],[19,4,19,5],[20,2,20,3],[20,4,20,5],[21,2,21,3],[21,4,21,5],[22,2,22,3],[22,4,22,5],[23,2,23,3],[23,4,23,5],[24,2,24,3],[24,4,24,5],[25,2,25,3],[25,4,25,5],[26,2,26,3],[26,4,26,5],[27,2,27,3],[27,4,27,5],[28,2,28,3],[28,4,28,5],[29,2,29,3],[29,4,29,5],[30,2,30,3],[30,4,30,5],[31,0,31,5],[32,0,32,2],[32,3,32,4],[32,5,32,6],[33,0,33,2],[33,3,33,4],[33,5,33,6],[34,0,34,2],[34,3,34,4],[34,5,34,6]]}
["措施项目清单报价表（一）"]
["工程名称：厚街镇厚山现代化产业园产业空间开发项目新建3台630kVA临时箱变安装工程",{"$nulls":4},"(编制单位盖章)"]
["序号","项目名称","计算基础",null,"费 率（%）",null,"金额\n（元）"]
["1","绿色施工安全防护措施费"]
["LSSGCSF00001","绿色施工安全防护措施费","分部分项人工费+分部分项机具费",null,"35.77"]
["2","措施其他项目"]
["031301010001","安装与生产同时进行增加费用","分部分项人工费",null,"0"]
["031301011001","在有害身体健康环境中施工增加费","分部分项人工费",null,"0"]
["TSSGBWZJF001","在地下（暗）室、设备及大口径管道内等特殊施工部位进行施工增加费",null,null,"30"]
["粤031302008001","赶工措施费","分部分项人工费+分部分项机具费",null,"0"]
["031302002001","夜间施工增加费",null,null,"20"]
["JTGRSGZJF001","交通干扰工程施工增加费",null,null,"10"]
["粤031302009001","文明工地增加费","分部分项人工费+分部分项机具费",null,"0"]
["DXGXJCJXF001","地下管线交叉降效费"]
["QTFY00000001","其他费用"]
{"$rows_empty":16}
["合    计"]
["注：本表适用于以“项”计价的措施项目"]
["编制人：                                       证号：",{"$nulls":4},"编制日期："]
[{"$nulls":5},"第 1 页  共 1 页"]

{"sheet":"（清单）措施项目清单报价表（二）","index":3,"n_rows":35,"n_cols":10,"rows_kept":35,"merged":[[0,0,0,9],[1,0,1,4],[1,6,1,9],[2,0,3,0],[2,1,3,1],[2,2,3,2],[2,3,3,3],[2,4,3,6],[2,7,3,7],[2,8,2,9],[4,4,4,6],[5,4,5,6],[6,4,6,6],[7,4,7,6],[8,4,8,6],[9,4,9,6],[10,4,10,6],[11,0,11,8],[12,4,12,6],[13,4,13,6],[14,4,14,6],[15,4,15,6],[16,4,16,6],[17,4,17,6],[18,4,18,6],[19,0,19,8],[20,4,20,6],[21,4,21,6],[22,4,22,6],[23,4,23,6],[24,4,24,6],[25,4,25,6],[26,4,26,6],[27,4,27,6],[28,4,28,6],[29,4,29,6],[30,0,30,8],[31,0,31,8],[32,0,32,4],[32,6,32,9],[33,0,33,4],[33,6,33,9],[34,0,34,4],[34,6,34,9]]}
["措施项目清单报价表（二）"]
["工程名称：厚街镇厚山现代化产业园产业空间开发项目新建3台630kVA临时箱变安装工程",{"$nulls":5},"(编制单位盖章)"]
["序号","编码","项目名称","项目特征","计量\n单位",null,null,"工程数量","金额（元）"]
[{"$nulls":8},"综合单价","合价"]
[1,"1","绿色施工安全防护措施费"]
["1.1","1.1","综合脚手架",null,"项",null,null,"1"]
["1.2","1.2","施工现场围挡和临时占地围档",null,"项",null,null,"1"]
["1.3","1.3","施工围档照明",null,"项",null,null,"1"]
["1.4","1.4","防尘降噪绿色施工防护棚",null,"项",null,null,"1"]
["1.5","1.5","施工便道",null,"项",null,null,"1"]
["1.6","1.6","样板引路",null,"项",null,null,"1"]
["小  计"]
[2,"2","措施其他项目"]
["2.1","2.10","模板工程",null,"项",null,null,"1"]
["2.1.1","041102001001","垫层模板","1.构件类型:垫层模板\n2.符合设计图纸、施工规范要求","m2",null,null,"272.01"]
["2.1.2","041102002001","基础模板","1.构件类型:基础模板\n2.符合设计图纸、施工规范要求","m2",null,null,"616.44"]
["2.1.3","041102033001","井顶(盖)板模板","1.构件类型:预制盖板模板\n2.符合设计图纸、施工规范要求","m3",null,null,"3.35"]
["2.2","031302007001","高层施工增加",null,"项",null,null,"1"]
["2.3","031301017001","脚手架搭拆费",null,"项",null,null,"1"]
["小  计"]
{"$rows_empty":10}
["本页小计"]
["合  计"]
["注：本表使用于以综合单价形式计价的措施项目"]
["编制人：                                   证号：",{"$nulls":5},"编制日期："]
[{"$nulls":6},"第 1 页  共 1 页"]